## Slide 1: WFI System
Pretreatment
(Nanofiltration & UV Sterilization, Conductivity)
Polishing
(Reverse Osmosis)
Multi Step Distillation
WFI
Storage
POUs
POUs
QC
Pump
Pump
Distillation
Column
POUs
Clean Steam
PW
Storage
HE
HE
Feed Water
HE
Notes: QC: Probennahme
PW: purified Water
He: Heater

## Slide 2: Characteristics
Minimize dead legs -> avoid stagnant of water
Material = Stainless Steel 316L
Constant turbulent flow
Positive pressure between the loop and Points of use (POUs)
Adequate slope of piping toward the drains
Air breaks to wastewater
7. Two pumps for redundancy
Pumps between -> Nano & Reverse Osmosis
-> PW storage and loop (twice)
-> WFI storage and loop (twice)

## Slide 3: Points Of Uses / Interceptions -> see excel
Flows | USP | DSP | Buffer & Media Preparation
Feed Water |  |  | 
PW |  |  | 
WFI |  |  | 
Clean Steam |  |  | 
Process Air (clean) |  |  | 
Compresses Cleaned Air |  |  | 
Process Gases |  |  | 
Liquid Nitrogen |  |  | 

## Slide 4: Points Of Uses -> see excel
USP | DSP | Buffer & Media Preparation

## Slide 5
Equipments Clean Utilities
PW | WFI | Clean Steam | Clean Compressed air | Process Air (HVAC) | Process Gases (N2, O2, CO2,H2O2) | Liquid Nitrogen
Inside | Inside | Inside | Inside | Inside | Outside | Outside
Heat exchanger | Heat exchanger | Distillation Column | Filters | Filters | Storage Tanks for all gases | Storage Tank
Storage Tank | Storage Tank | Compressor | Pneumatic Valve | Cooler | Pneumatic Valve | Pneumatic Valve
Reverse Osmosis | Distillation Column |  | Storage | Heater + Reheaters |  | 
Nano Filtration |  |  | Compressor | Humidifier |  | 
 |  |  |  | Mixing Chambers |  | 
For Feed Water -> small extra tank???

## Slide 6
Product | WFI Volume (per batch) [L] (DSP) | Buffer Volume [L] | Buffer volume (125%) [L] | PW (USP)
Product A | 3541 | 35962 | 44952 | 2500
Product B | 3541 | 35435 | 44294 | 2500
Product C | 3616 | 34770 | 43462 | 2500
Product D | 3541 | 36671 | 45838 | 2500
Total | 14239 | 142838 | 178546 | 10000
Estimation from the Process Description file -> Waiting for feedback from DSP and B&M Prep
WFI / PW Estimation

## Slide 7: appendix

## Slide 8
Just as help

## Slide 9
Just as help

## Slide 10
Just as help

## Slide 11
D Class
C Class
CNC
NC
Administration
Personnel Airlock
Inoculum
Personnel Airlock
USP Production
Quality Control
DSP freezing
DSP V-
DSP V+
Liquid Waste
Product
Waste
Material
Media prep
Buffer prep & storage
Corridor
Material Airlock
USP harvest
Media
storage
Corridor
Personnel Airlock
Personnel Airlock
Personnel Airlock
Material Airlock
Corridor
DSP Storage
Process Gases (N2, O2, CO2)
Personal
Solid Waste
Biological Liquid Waste
Clean Steam
Process Air
WFI
PW
Cooling Water
Clean Compressed Air
PA
PA
PA
PA
PA
Personnel Airlock
PA
PA
Notes: noice

## Slide 13
Waste Management
Engineering
Stairs
Elevator
WFI & Steam Production
Electricity & Emergency Generators
Data Storage
PW and Feed Water
Stairs
Elevator
Notes: Basement

## Slide 14
Administration
Personnel Airlock
USP Production
Quality Control
DSP storage
DSP Polishing V+
DSP V-
DSP V+
Buffer storage
Corridor
Material Airlock
Warehouse
USP harvest
Buffer prep
Corridor
Personnel Airlock
Personnel Airlock
Personnel Airlock
Personnel Airlock
Material Airlock
Corridor
Stairs
Elevator
Stairs
Elevator
Material Airlock
Text hinzufügen
Notes: Basement

## Slide 15
2. floor
1. floor
Ground floor
Basement
Warehouse
Storage
Containment
Upstream
Downstream
1 m
5 m
5 m
Buffer prep.
3 m
5 m
The Office
7 m
HVAC
Entrance
Personnel/
Material airlock
Crawl space
3 m

## Slide 16
PRESENTATION

## Slide 17
Clean Utilities
 | WFI Volume per batch [L] | PW Volume per batch [L] | Solid Waste Volume per batch [L] | Liquid Waste Volume per batch [L] | Liquid Biological Waste per batch [L]
DSP | 3541 | - | 625 | 42000 | -
USP | - | 2500 | - | - | 2500

## Slide 18
Equipments Clean Utilities
PW | WFI | Clean Steam | Clean Compressed air | Process Air (HVAC) | Process Gases (N2, O2, CO2) | Liquid Nitrogen
Basement | Basement | Basement | Basement | 2.nd Floor | Outside | Outside
Heat exchanger | Heat exchanger | Distillation Column | Filters | Filters | Storage Tanks for all gases | Storage Tank
Storage Tank | Storage Tank | Compressor | Pneumatic Valve | Cooler | Pneumatic Valve | Pneumatic Valve
Reverse Osmosis | Distillation Column |  | Storage | Heater + Reheaters |  | 
Nano Filtration |  |  | Compressor | Humidifier |  | 
Water Treatment |  |  |  | Mixing Chambers |  | 
Notes: We did a list of the main equiptment used for the clean utilities and where it is

## Slide 19
HVAC And Points Of Use Zone Concept

## Slide 20
Points Of Uses

## Slide 21
WFI & PW and
Clean Steam System

## Slide 22
Notes: Valve missing, probennahme